## ANALYSIS
PLUMBING DESIGN ANALYSIS
PROJECT:
LOCATION:
I. | DAILY WATER DEMAND
| Number of Occupants |  |  |  |  | 6 | Pax
| Daily Water Demand per Person |  |  |  |  | 45 | Gallons
| Total Water Demand |  |  |  |  | 270 | Gallons
II. | SIZE OF CISTERN / WATER STORAGE (good for 3 days)
Cistern/H2O Storage = Total Water Demand X 300%
|  | = | 270 | Gallons | X | 300 | %
|  | = | 810 | Gallons
|  | = | 3.0662 | M3
2.94
| Therefore use: |  | 1.5 | M Length
|  |  | 1.5 | M Width
|  |  | 1.4 | M Height
|  |  | 3.15 | M3 Cistern Volume
or Best Tank 853 Gallons Capacity / Code 3200
***Based on the available water tank (BEST TANK) in the market provided with Stainless Ball / Float Valve.
III. | SIZING OF ELEVATED WATER TANK (good for 1.5 days)
Overhead Tank = Total Water Demand X 150%
|  | = | 270 | Gallons | X | 150 | %
|  | = | 405 | Gallons
Based on the available water tank (BEST TANK) in the market provided with Float Switch.
| Therefore use: |  | Best Tank 400 Gallons Capacity / Code1500
IV. | RECOMMENDED WATER PUMP (Good for 2 to 5 Storey Building)
3/4HP to 1HP CENTRIFUGAL PUMP at flow rate of 52 l/m, max head 52 m
V. | SIZING OF DRAINAGE & VENT PIPES
Drainage Fixture Unit (DFU) Values
|  | FIXTURE | UNIT | DFU | Total DFU
|  | Water Closet | 2 | 3 | 6
|  | Lavatory | 2 | 2 | 4
|  | Shower | 2 | 2 | 4
|  | Urinal | 0 | 2 | 0
|  | Bath Tub | 0 | 2 | 0
|  | S/F Drain | 6 | 2 | 12
|  | Kitchen Sink | 2 | 2 | 4
|  | Total |  |  | 30
NOTE: If the result is NOT more than 256 DFU use 50 mm Ø for vent & waste pipes & 100 mm Ø for soil & sewer pipes.
| Therefore use: |  | 50 mm Ø uPVC (#2) for Ventilation and Waste Pipes.
100 mm Ø uPVC (#4) for Soil, Sewer, and Drain Pipes.
150 mm Ø uPVC (#6) for Storm Drainage Pipes.
***As per Uniform Plumbing Code 2000 & RNPCP 1999
VI. | SIZING OF GUTTER & DOWNSPOUT
Table for Leader (Gutter) / Downspout as per UPC 2000 & RNPCP 1999
Maximum Allowable Projected Roof Areas (Rainfall Intensity)
|  | 150 mm / hr | Pipe Size of Downspout
|  | 34 M2 | #2 or 50 mm Ø uPVC Pipe
|  | 100 M2 | #3 or 80 mm Ø uPVC Pipe
|  | 214 M2 | #4 or 100 mm Ø uPVC Pipe
|  | 389 M2 | #5 or 125 mm Ø uPVC Pipe
|  | 632 M2 | #6 or 150 mm Ø uPVC Pipe
|  | Building Roof Area: |  | 102.5 | M2
The table shows that the nearest value for Roof Area of 102.5 M2 is 100 M2 which is equal to #3 or 80 mm Ø uPVC.
| Therefore use: |  | #3 or 80 mm Ø uPVC Pipe DOWNSPOUT is safe at maximum
of 5m span of column.
Table for Gutter 11-3 as per UPC 2000
|  | 150 mm / hr | Diameter of Gutter
|  | 21 M2 | 80 mm
|  | 44.6 M2 | 100 mm
|  | 77.5 M2 | 125 mm
|  | 118.9 M2 | 150 mm
|  | 170.9 M2 | 175 mm
|  | 246.7 M2 | 200 mm
|  | 445.9 M2 | 250 mm
|  | Building Roof Area: |  | 102.5 | M2
The table shows that the nearest value for Roof Area of 102.5 M2 is 118.9 M2 which is equal to 150 MM.
| Therefore use: |  | 150 mm diameter of GUTTER design is safe.
VII. | SIZING OF SEPTIC TANK
Table for Septic Tank Table K-2 as per UPC 2000
Tank Volume UPC 2000
|  | Bedroom | Gallons | M3
|  | 2 | 750 | 2.84
|  | 3 | 1000 | 3.79
|  | 4 | 1200 | 4.54
|  | 5 to 6 | 1500 | 5.68
Allowable Dimension of Septic Tank:
|  |  | 4 | M Length
|  |  | 1.2 | M Width
|  |  | 1 | M Depth
|  |  | 4.8 | M3 Tank Volume
VIII. | SIZING OF SWIMMING POOL PUMP, FILTER, & PIPES
Number of Gallons of H2O in the Rectangular Pool
Average Depth = (Shallow + Deep) /2
|  |  | 1 | 1.5
|  | 4 | 3 | 5 | 2
Gallons = L x W x Ave. Depth x 7.5
|  |  | 4.5 | 8
|  | 11700 | 15 | 26 | 7.5
Note: Units are in English System (Feet)
Calculate Gallons per Hour to pump water in 8 hrs
GPH = No. of Gallons / 8
|  | 1463 | 11700 | 8
Convert GPH to GPM
GPM = GPH / 60
|  | 24 | 1463 | 60
Calculate the Average Feet of Head
AFH =Total Run of Pipe / 3
25
|  | 27 | 82 | 3
| Therefore use: |  | Pool Pump at1/2 hp, 230v, 60hz. @ least 30 GPM at 30 Feet of Head
with Skimmer good for 500 square foot pool
Sizing Water Filter at 25% Oversize from the Pool Pump
Water Filter = GPM x 1.25
|  | 67.5 | 30 | 1.25
| Therefore use: |  | Pool Filter that is good for 50 GPM
Determine the Pipe Size
PIPE SIZES
|  | 50MM Ø PPR PN20 | Max. Flow Rate of 60 GPM
|  | 63MM Ø PPR PN20 | Max. Flow Rate of 100 GPM
|  | 75MM Ø PPR PN20 | Max. Flow Rate of 140 GPM
| Therefore use: |  | 50MM Ø PPR PN25 PIPE or 1 1/2" Ø PVC Pipe
Prepared by:
SUNNY B. OJEDA, RMP
D
Note on E35: DFU as per UPC 2000
Note on F43: If the result is MORE than 256 DFU use 80 mm dia for vent & waste pipes & 100-125 mm dia for soil, sewer, and drain pipes
Note on F86: SEPTIC TANK shall be at minimum of 1.50 m in length and 0.90 m in width. Liquid depth shall be not less than 0.75 m depth nor more than 1.80 m.
Note on C125: 1 1/2", 2", 2 1/2" PVC
Note on F155: SEPTIC TANK shall be at minimum of 1.50 m in length and 0.90 m in width. Liquid depth shall be not less than 0.75 m depth nor more than 1.80 m.

## TABLES
BEST TANK |  | Pump Output (GPM) vs. Total Resistance To Flow (Feet of Head)
206 gal | Code775 | Model Number | 10 ft | 20 ft | 30 ft | 40 ft | 50 ft
400 gal | Code1500 | SP1750 | 55 | 45 | 33 | 15 | -----
526 gal | Code2000 | SP1775 | 65 | 57 | 45 | 30 | -----
700 gal | Code2600 | SP1780 | 78 | 69 | 56 | 40 | 15
853 gal | Code3200
1207 gal | Code4600 | POOL Pump Output (GPM) vs. Total Resistance To Flow (Feet of Head) HAYWARD
1572 gal | Code6000 | Model No. Max Rated | 20 ft | 30 ft | 40 ft | 50 ft | 60 ft | 70 ft
2028 gal | Code7700 | SP2600X5 (1/2 HP) | 55 | 45 | 29 | -- | -- | --
3403 gal | Code12800 | SP2605X7 (3/4 HP) | 67 | 58 | 47 | 31 | -- | --
4000 gal | Code15000 | SP2607X10 (1 HP) | 85 | 76 | 65 | 50 | 27 | --
|  | SP2610X15 (1.5) | 97 | 90 | 80 | 67 | 50 | 10
|  | SP2615X20 (2 HP) | 116 | 111 | 99 | 85 | 70 | 51
|  | SP2621X25 (2.5 HP) | 109 | 109 | 104 | 95 | 84 | 69
https://www.hayward-pool.com/shop/en/pools/1-2-hp-super-pump-sp2600x5
https://blog.intheswim.com/swimming-pool-feet-of-head-calculations/

## CENTRI PUMP
AVIVA
PRIMA
EUROSTAR
JR. KAWASAKI | JAPAN
M. AQUA | ITALY
TOLSEN | EUROPE
GOULDS | USA
CENTRIFUGAL PUMP Model 0.5HP, 0.75HP, and 1.0HP JP w/o Bladder
1/2HP at 370W with max. flow rate 47 l/m, max. head 47 m
3/4HP at 550W with max. flow rate 52 l/m, max head 52 m
1HP at 750 with max. flow rate 56 l/m, max head 56 m