## MY PROJECT
SCHEDULE OF LOADS | [14 empty] | COMPUTATION OF LOAD
CIRCUIT | DESCRIPTION | LIGHTING | CONV | SWITCHES |  |  |  | VOLT | AMPERE | A.POWER (VA) | SIZE OF WIRE | SIZE OF CONDUIT | CB RATING |  | Contiuous Loads |  |  |  | = |  |  | 41.7391 | Ampere
NUMBER |  | OUTLET | OUTLET | S1 | S2 | S3 | S3W |  |  |  | in sq. mm (TW/THW Cu.) | in mm dia. (PVC) | POLE | AMP-TRIP | Non-Contiuous Loads |  |  |  | = |  |  | 43.3913 | Ampere
1 | LIGHTING | 12 | [5 empty] | 230 | 5.22 | 1200 | #14 AWG or 2.0 sq mm | 20 | 2 | 15 | Total Loads |  |  |  | = |  |  | 85.1304 | Ampere
2 | LIGHTING | 15 | [5 empty] | 230 | 6.52 | 1500 | #14 AWG or 2.0 sq mm | 20 | 2 | 15 | MAIN FEEDER
3 | CONVENIENCE OUTLET |  | 8 |  |  |  |  | 230 | 12.52 | 2880 | #12 AWG or 3.5 sq mm | 20 | 2 | 20 | Main Feeder Current = (CL X 100%) + (NCL X 125%)
4 | CONVENIENCE OUTLET |  | 10 |  |  |  |  | 230 | 15.65 | 3600 | #12 AWG or 3.5 sq mm | 20 | 2 | 20 |  | = | ( | 41.7391 | X 100% ) | + | ( | 43.3913 | X 125% )
5 | 3.5kW Tankless Water Heater |  | 3.5 |  |  |  |  | 230 | 15.2 | 3500 | #10 AWG or 5.5 sq mm | 25 | 2 | 30 |  | = |  | 95.9783 | Ampere
6 | 2 hp A.C.U. | [6 empty] | 230 | 12 | 2760 | #10 AWG or 5.5 sq mm | 25 | 2 | 30 | Therefore use |  |  | 2- | #1 AWG or 38.0 sq mm |  |  |  | TW Cu Wire
7 | 1.5 hp A.C.U. | [6 empty] | 230 | 10 | 2300 | #12 AWG or 3.5 sq mm | 25 | 2 | 20 | plus | 1 - #4 AWG or 22 sq mm TW Cu Wire
8 | 1 hp Water Pump | [6 empty] | 230 | 8 | 1840 | #12 AWG or 3.5 sq mm | 25 | 2 | 20 |  | inside 38 mm diameter RSC with
9 | SPARE | [6 empty] | 230 | - | - | - | - | - | - | Grounding Conductor |  |  |  | 8.0 sq mm |  |  | Copper
10 | SPARE | [6 empty] | 230 | - | - | - | - | - | - | RATING OF MAIN CIRCUIT BREAKER @ 80% DF
[9 empty] | AMP | VA | [5 empty] | Use |  | 2 Pole | 125 |  |  | Ampere Trip Circuit Breaker
[9 empty] | 41.7391 | 9600 | for Continuous Loads |  |  |  | TYPE OF SERVICE
TOTAL |  | 27 | 18 | 0 | 0 | 0 | 0 |  | 43.3913 | 9980 | for Non-continuous Loads |  |  |  | SINGLE PHASE, 2W, 230V, 60 Hz
| CHECK THE ELECTRICAL PLANS Problem: Determine the size of branch circuit wires for lighting outlets, convenience outlets, Water Heater (Tankless), Air-Con Units, and Water Pump with the corresponding size of conduit pipes and rating of circuit breaker. Compute the total loads and determine the size of conductor for main feeder, main circuit breaker, size of conduit, and grounding conductor. | [11 empty] | GUIDELINES & NOTES
` | [11 empty] | 1 | THE NUMBER CONVENIENCE OUTLET W/ 2-PLUG IN ONE (1) CIRCUIT MUST
NOT BE MORE THAN 10 FIXTURES SO THAT #12 AWG or 3.5 SQ.MM. TW cu WIRE COULD SUSTAIN THE LOAD.
[12 empty] | 2 | THE NUMBER LIGHTING OUTLET IN ONE (1) CIRCUIT MUST
NOT BE MORE THAN 15 FIXTURES SO THAT #14 AWG or 2.0 SQ.MM. TW cu WIRE COULD SUSTAIN THE LOAD.
[12 empty] | 3 | DIVIDE WATTAGE BY 230V TO GET THE AMPERE FOR WATER HEATER
[12 empty] | 4 | MOTOR LOADS SHALL BE COMPUTED AT 250% DEMAND FACTOR TO GET THE APPROPRIATE CB.
[12 empty] | 5 | FEEDER CURRENT SHALL BE THE SUM OF CONT. LOAD MULTIPLIED BY 100% AND NON-CONT. LOAD MULTIPLIED BY 125%
Note on L3: apparent power the unit is volt-ampere
Note on M3: TW = moisture resistant thermoplastic (DW) THHN = heat resistant thermoplastic (D) THW = moisture & heat resistant thermoplastic (DW) T = thermoplastic (DW) RHW = moisture & heat resistant rubber (DW)
Note on I4: 3-way switch
Note on C5: 12A is the maximum amperage capacity of 15A circuit breaker so the min. wire size is #14 AWG and the max. LO is 15 according to PEC "NEC/PEC provides that the connected load in the CB shall not exceed to 80% amperage capacity" P = LO X 100 Amp = no. of outlet x 100/230
Note on K5: no. of outlet x 100/230
Note on K6: no. of outlet x 100/230
Note on C7: 16A is the maximum amperage capacity of 20A circuit breaker, so the min. wire size is #12 AWG and the max. CO is 10 Rule of Thumb: Assign max. draw of 1.5amp to each on receptacles w/c allows 10 on a 20amp circuit. "NEC/PEC provides that the connected load in the CB shall not exceed to 80% amperage capacity" P(VA)=(ConOx2) x 180 Amp =(ConOx2) x 180/230
Note on K7: no. of outlet x 180/230
Note on K8: no. of outlet x 180/230
Note on C9: 3.5kW WH or 3500VA/230V is equal to 15.20A and the maximum amperage capacity is 20% Let's try 20AT CB x 80% = 16A Therefore 20AT is safe since 15.20A is not higher
Note on E9: HIDDEN VALUE
Note on K9: 3500W / 230V Divide watts by volts to get amps.
Note on C10: 12A x 250% protection factor for motor= 30A therefore use 30AT CB
Note on K10: See table of AC Motor Full Load Current
Note on W10: SEE TABLE for AMPICITY CONDUCTORS As per PEC the minimum size of wire for main feeder should not be less than #10AWG
Note on C11: 10A x 250% protection factor for motor= 25A therefore use 30AT CB
Note on K11: Sirsun: See table of AC Motor Full Load Current
Note on T11: CAHANGE with at least half size of main conductor
Note on C12: 8A x 250% PF = 20A therefore use 20AT CB
Note on K12: See table of AC Motor Full Load Current
Note on S12: dependent to size of wire see RSC conduit table
Note on W13: SEE TABLE dependent to circuit breaker
Note on W15: SEE TABLE dependent to MFCurrent
Note on M16: LO, tank-WH, WPump & ACU Cont. Load is one where the maximum current is expected to run for 3 hrs or more.
Note on M17: CO, tankless-WH, F
Note on S17: Sirsun: Standard for RESIDENTIAL BLDG.

## TABLES
AMPACITY CONDUCTORS / WIRE SIZING
|  | AMP range |  | TW Cu Wire | RSC φ
Full Load Current of AC Motors |  | 1 | 15 | #14 AWG or 2.0 sq mm |  | AMP RATING FOR CIRCUIT BREAKER @ 80DF |  |  | Grounding Conductor
HP | Full Load Amp. | 15.1 | 20 | #12 AWG or 3.5 sq mm |  | AMPERAGE range |  | Ampere Trip CB | overcurrent pro/CB | Copper in sq mm
0.166 | 2.2 | 20.1 | 30 | #10 AWG or 5.5 sq mm | inside 25 mm diameter RSC with | 1 | 12 | 15 | 15 | 2.0 sq mm
0.25 | 2.9 | 30.1 | 40 | #8 AWG or 8.0 sq mm | inside 32 mm diameter RSC with | 13 | 16 | 20 | 20 | 3.5 sq mm
0.33 | 3.6 | 40.1 | 55 | #6 AWG or 14.0 sq mm | inside 32 mm diameter RSC with | 17 | 24 | 30 | 30 | 5.5 sq mm
0.5 | 4.9 | 55.1 | 70 | #4 AWG or 22.0 sq mm | inside 38 mm diameter RSC with | 25 | 32 | 40 | 40 | 5.5 sq mm
0.75 | 6.9 | 70.1 | 90 | #2 AWG or 30.0 sq mm | inside 38 mm diameter RSC with | 33 | 40 | 50 | 60 | 5.5 sq mm
1 | 8 | 90.1 | 100 | #1 AWG or 38.0 sq mm | inside 38 mm diameter RSC with | 41 | 48 | 60 | 80 | 8.0 sq mm
1.5 | 10 | 100.1 | 120 | #0 AWG or 50.0 sq mm | inside 50 mm diameter RSC with | 49 | 64 | 80 | 100 | 8.0 sq mm
2 | 12 | 120.1 | 135 | #00 AWG or 60.0 sq mm | inside 50 mm diameter RSC with | 65 | 80 | 100 | 200 | 14.0 sq mm
3 | 17 |  |  |  |  | 81 | 100 | 125 | 300 | 22.0 sq mm
5 | 28 | AT CB | THW | RSC / PVC φ |  | 101 | 120 | 150 | 400 | 30.0 sq mm
7.5 | 40 | 15 | #14 AWG or 2.0 sq mm | 20 | 4 wires max | 121 | 140 | 175 | 600 | 38.0 sq mm
10 | 50 | 20 | #12 AWG or 3.5 sq mm | 25 | 4 wires max | 141 | 160 | 200 | 800 | 50.0 sq mm
|  | 30 | #10 AWG or 5.5 sq mm | 25 | 3 wires max | 161 | 180 | 225 | 1000 | 60.0 sq mm
|  | 40 | #8 AWG or 8.0 sq mm | 32 | 3 wires max | 181 | 200 | 250
|  | 50 | #6 AWG or 14.0 sq mm | 32 | 3 wires max
|  | 80 | #4 AWG or 22.0 sq mm | 38 | 3 wires max
|  | 100 | #2 AWG or 30.0 sq mm | 38 | 3 wires max
|  | 125 | #1 AWG or 38.0 sq mm | 38 | 3 wires max
|  | 150 | #0 AWG or 50.0 sq mm | 50 | 3 wires max
|  | 175 | #00 AWG or 60.0 sq mm | 50 | 3 wires max
Note on G4: #10 AWG is the minimum for main feeder
Note on F16: #10 AWG is the minimum for main feeder